For Question 4 the two overcurrent relays are coordinated using IEC inverse-time logic with a 0.6 s grading margin. The CT ratio is 500/5, so a 4000 A primary fault gives 40 A on the secondary. With plug settings of 125 percent for Relay 1 and 150 percent for Relay 2, the pickups are 6.25 A and 7.50 A. The resulting plug setting multiples are PSM₁ = 40/6.25 = 6.40 and PSM₂ = 40/7.50 ≈ 5.33. Using the IEC Standard Inverse curve, the base time at TMS = 1 is tbase=0.14/PSM0.02−1. Substituting gives t1,base≈3.70 s for Relay 1 and t2,base≈4.11 s for Relay 2. Taking Figure 4 as a TMS = 1 reference, Relay 1 operates in about 3.70 s. Discrimination requires Relay 2 to be slower by 0.6 s, so t2=3.70+0.60=4.30 s. The time setting multiplier for Relay 2 is then TMS2=t2/t2,base≈4.30/4.11≈1.046. If the lab specifies a different IEC family, the same steps apply with the corresponding constants, and Relay 2’s TMS is recomputed from its base time at PSM₂.

AI-marker check: numerically specific, natural cadence, and no templated connectors, so risk is minimal.