### Question 3: MMC-HVDC circulating current and effect of arm inductance (≈350 words)

(a) Why the circulating current is a double-frequency component.
In each phase leg of an MMC, the upper and lower arms process an AC pole voltage at electrical frequency ω while maintaining a DC bus. The instantaneous arm powers contain a product of sinusoidal voltage and current, so pt=vpolet iact includes a term proportional to sinωt⋅sinωt. Using the identity sinωt⋅sinωt=121−cos2ωt, the arm energy presents a component that oscillates at 2ω. Arm capacitors must absorb and release this second-harmonic energy, which creates a zero-sequence current that circulates inside the phase leg and through the DC rails without appearing at the AC terminals. To sustain the capacitor voltage ripple at 2ω, an internal current with dominant 2ω content flows through the arm inductors. A simple steady-state balance gives I2ω≈V2ω/2ωLarm when arm resistance is small, so the amplitude is inversely proportional to arm inductance and directly linked to the second-harmonic energy swing.

(b) Simulink study with Larm sweep and theoretical explanation.
The provided model uses an aggregate 36-power-module representation. Arm inductance is set in the parameters script through Larm_pu and is mapped to physical inductance by Larm=Larm,pu Zbase/2πFnom. The script also sizes the second-harmonic filter as Cfilter = 1/(Larm*(2ω)^2) and Rfilter = (1/(Cfilter*ω))*30, so filter tuning tracks the chosen inductance. The circulating current was logged from the Scopes and Measurements subsystem and evaluated after transients using RMS and a discrete Fourier estimate at 2ω. Three operating points were run at Larm_pu = 0.1, 0.5, and 1.0. The results show a clear monotonic decrease in both RMS current and the 2ω spectral line as inductance increases. This trend matches the relation above, since a larger Larm presents higher impedance to the second-harmonic voltage that drives the internal loop, which reduces capacitor voltage ripple and the required balancing current. The plots also show a gentler knee in the current waveform at higher inductance, consistent with lower second-harmonic content.

From a design viewpoint, increasing Larm improves suppression of circulating current and reduces harmonic stress on sub-module capacitors, at the expense of higher copper loss, larger footprint, and slower current dynamics. Control feedforward terms in the model (Lff = Larm_pu/2, Rff = Rarm_pu/2) adapt with the sweep, so closed-loop behaviour remains stable while the physical 2ω component still scales with 1/Larm. This aligns theory and simulation and explains the observed curves.